Typical Specification

CST-SPEC-01

Typical Specification for Lochinvar® Cogeneration Storage Tank

The COGENERATION STORAGE TANK shall be a Lochinvar Model CST150 or CST150-DHW with vertical construction having a capacity of 150 gallons.

The COGENERATION STORAGE TANK shall be constructed in accordance with ASME Boiler and Pressure Vessel Code Section VIII Div. 1, Part U requirements, stamped and registered with the National Board of Boiler and Pressure Vessel Inspectors.  The tank shall be furnished with 2” NPT connections for system supply and return. One 1” relief valve tapping; and one 1” drain pipe shall be supplied. The tank shall be constructed with a built in air separator with automatic air vent.

The COGENERATION STORAGE TANK shall have a working pressure of 125 PSI. The COGENERATION STORAGE TANK shall carry a five year limited warranty against tank failure resulting from defects in materials or workmanship (see warranty for details).

The COGENERATION STORAGE TANK shall be constructed with a heavy gauge galvanized steel jacket assembly,  primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mills. The jacket dimensions shall be 28.5" diameter, and 74.8" tall.

The COGENERATION STORAGE TANK shall be completely encased in a minimum of 2" thick, high density, HCFC free, polyurethane foam insulation to meet the energy efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.

The COGENERATION STORAGE TANK shall be furnished with a Storage Controller and four sensors. The tank will be constructed with four bulb wells installed in ¾” NPT tapings.

The COGENERATION STORAGE TANK CST150-DHW shall be furnished with an internal DHW coil for DHW applications. Connection sizes shall be 1” NPT. The DHW coil shall provide a minimum domestic hot water delivery of 3 GPM @ 100º rise when the tank is supplied with 150,000 BTU/hr. from the Cogeneration system. The DHW coil shall provide a maximum domestic hot water delivery of 17 GPM @ 100º rise when the tank is supplied with 850,000 BTU/hr. from the Cogeneration system supplemented with an axillary heater.

01/19 – Printed in U.S.A.