Copyright 2009 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235216 – FIRE-TUBE CONDENSING BOILERS

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes packaged, factory-fabricated and assembled, gas-fired, fire-tube condensing boilers, trim, and accessories for space heating hot water.

      - SUBMITTALS

        - Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

        - Shop Drawings:  For boilers, boiler trim, and accessories.

          - Include plans, elevations, sections, details, and attachments to other work.

          - Wiring Diagrams: Power, signal, and control wiring.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

Retain subparagraph below if equipment includes wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

        - Source quality-control test reports:  Indicate and interpret test results for compliance with performance requirements before shipping.

        - Field quality-control test reports:  Indicate and interpret test results for compliance with performance requirements.

        - Warranty:  Standard warranty specified in this Section.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data:  For boilers to include in emergency, operation, and maintenance manuals.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction.  Also, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

        - ASHRAE/IESNA 90.1 Compliance:  Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Delete first paragraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

        - AHRI Compliance:  Boilers shall be AHRI listed and must meet the minimum efficiency specified under AHRI BTS-2000 as defined by Department of Energy in 10 CFR Part 431.

        - ANSI Compliance:  Boilers shall be compliant with ANSI Z21.13 test standards for US and Canada.

        - CSA Compliant:  Boilers shall be compliant with CSA certification.

      - COORDINATION

        - Coordinate size and location of concrete bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 23 Section "Heating Boilers."

        - Standard Warranty:  Boilers shall include manufacturer's standard form in which manufacturer agrees to repair or replace components of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

          - Warranty Period for Fire-Tube Condensing Boilers:

            - Heat Exchanger, Pressure Vessel and Condensation Collection Basin shall carry a 10 year limited warranty against defects in materials or workmanship and failure due to thermal shock.

            - All other components shall carry a one year warranty from date of boiler start up.

- PRODUCTS

      - MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 23 Section "Heating Boilers" for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

        - Basis-of-Design Product:  Lochinvar Knight FTXL Boiler as specified on Drawings.  All others must be submitted by Voluntary alternate.

Retain one of four lists below.

Retain list below for pulse-combustion condensing boilers.

Retain list below for fire-tube condensing boilers.

Retain list below for water-tube condensing boilers.

Retain list below for water-jacketed condensing boilers.

Retain one of four "Manufactured Units" articles below.

      - CONSTRUCTION

Retain this article for fire-tube condensing boilers.

        - Description:  Boiler shall be natural gas fired, fully condensing, and fire tube design.  The boiler shall be factory-fabricated, factory-assembled, and factory-tested, fire-tube condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.

        - Heat Exchanger:  The heater exchanger shall bear the ASME “H” stamp for 160 psi working pressure and shall be National Board listed.  The heat exchanger shall be constructed of a fully welded stainless steel and of fire tube design.  The heat exchanger shall be designed for a single-pass water flow to limit the water side pressure drop.  Cast iron, aluminum, or condensing copper tube boilers will not be accepted.

        - Efficiency:  Boilers shall have an AHRI certified minimum thermal efficiency of 97 percent.

        - Condensate Collection Basin:  Fully welded stainless steel and shall include a stainless steel combustion analyzer test port.

        - Pressure Vessel:  The pressure vessel shall be in accordance with ASME Section IV pressure vessel code.  The pressure vessel shall be designed for a single-pass water flow to limit the water side pressure drop.  The pressure vessel shall contain a volume of water no less than:

| Model | Water Content |
| --- | --- |
| FTX400 | 13 gallons |
| FTX500 | 12 gallons |
| FTX600 | 12 gallons |
| FTX725 | 17 gallons |
| FTX850 | 16 gallons |
| FTX1000 | 19 gallons |

        - Burner:  Natural gas, forced draft single burner premix design.  The burner shall be high temperature stainless steel with a woven Fecralloy outer covering to provide modulating firing rates. The burner shall be capable of the stated gas train turndown without loss of combustion efficiency.

        - Blower:  Boiler shall be equipped with a pulse width modulating blower system to precisely control the fuel/air mixture to provide modulating boiler firing rates for maximum efficiency.  The burner firing sequence of operation shall include pre-purge, firing, modulation, and post-purge operation.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

          - Motors:  Comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

        - Gas Train:  The boiler shall be supplied with a negative pressure regulation gas train and shall be capable of the following minimum turndowns:

| Model | Turndown | Minimum Input | Maximum Input |
| --- | --- | --- | --- |
| FTX400 | 10:1 | 40,000 | 400,000 |
| FTX500 | 10:1 | 50,000 | 500,000 |
| FTX600 | 7:1 | 85,700 | 600,000 |
| FTX725 | 7:1 | 103,500 | 725,000 |
| FTX850 | 7:1 | 121,500 | 850,000 |
| FTX1000 | 10:1 | 99,900 | 999,000 |

        - Ignition:  Spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

        - High Altitude:  Boiler shall operate at altitudes up to 4,500 feet above sea level without additional parts or adjustments.  High altitude operation shall be certified at a minimum of 4,500 feet above sea level by a third party organization.  High altitude boilers shall be certified to 3,000 to 12,000 feet above sea level.  The boilers shall carry a CSA certification for high altitude operation up to 12,000 feet.

        - Casing:

          - Jacket:  Heavy gauge primed and painted steel jacket with snap-in closures.

          - Control Compartment Enclosures:  NEMA 250, Type 1A.

If retaining second option in "Jacket" Subparagraph above, delete first subparagraph below.

          - Insulation:  Minimum ½ inch thick, mineral fiber insulation surrounding the heat exchanger.

          - Combustion-Air Connections:  Inlet and vent duct collars.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

        - Characteristics and Capacities:

          - Heating Medium:  Hot water.

          - Design Water Pressure Rating:  160 psi working pressure.

          - Safety Relief Valve Setting:  50 psig

          - Minimum Water Flow Rate:

| Model | Minimum Flow |
| --- | --- |
| FTX400 | 10 gpm |
| FTX500 | 12 gpm |
| FTX600 | 15 gpm |
| FTX725 | 18 gpm |
| FTX850 | 21 gpm |
| FTX1000 | 30 gpm |

Retain one of first two subparagraphs below.

Retain one of two "Trim" articles below.

      - TRIM

Retain this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

        - Safety Relief Valve:

          - Size and Capacity:  50 lb.

          - Description:  Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

        - Pressure Gage:  Minimum 3-1/2 inch diameter.  Gage shall have normal operating pressure about 50 percent of full range.

        - Drain Valves:  Minimum NPS 3/4 or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

        - Condensate Neutralization Kit:  Factory supplied condensate trap with condensate trip sensor, high capacity condensate receiver prefilled with appropriate medium.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

      - CONTROLS

Retain paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC."

        - Refer to Division 23 Section "Instrumentation and Control for HVAC."

        - Boiler controls shall feature a standard, factory installed multi-color graphic LCD screen display with navigation dial and includes the following standard features:

          - Con-X-Us capable:  Boiler shall have the ability to communicate remotely using the optional Con-X-Us software via a wireless or Ethernet connection.

          - Variable Speed Boiler Pump Control:  Boiler may be programmed to send a 0-10V DC output signal to an ECM or VFD boiler pump to maintain a designed temperature rise across the heat exchanger.  The boiler shall be able to operate in this mode with a minimum temperature rise of 20 degrees F and a maximum temperature rise of 60 degrees F.  Project specific temperature rise shall be ____.

          - Password Security:  Boiler shall have a different password security code for the User and the Installer to access adjustable parameters.

          - Outdoor air reset:  Boiler shall calculate the set point using a field installed, factory supplied outdoor sensor and an adjustable reset curve.

          - Pump exercise:  Boiler shall energize any pump it controls for an adjustable time if the associated pump has been off for a time period of 24 hours.

          - Four pump control:  Boiler shall have the ability to control the boiler pump, a system pump, a domestic hot water pump, and a domestic hot water recirculation pump.

          - Ramp delay:  Boiler may be programmed to limit the firing rate based on six limits steps and six time intervals.

          - Boost function:  Boiler may be programmed to automatically increase the set point a fixed number of degrees (adjustable by installer) if the setpoint has been continuously active for a set period of time (time adjustable by installer).  This process will continue until the space heating demand ends.

          - Domestic hot water priority:  Boiler shall make the domestic hot water call for heat a priority over any space heating call and adjust the boiler setpoint to the domestic hot water boiler setpoint.

          - Domestic hot water modulation limiting:  Boiler may be programmed to limit the maximum domestic hot water firing rate to match the input rating of the indirect tank coil.

          - Domestic hot water night setback:  Boiler may be programmed to reduce the domestic hot water tank set point during a certain time of the day.

          - PC port connection:    Boiler shall have a PC port allowing the connection of PC boiler software.

          - Time clock:  Boiler shall have an internal time clock with the ability to time and date stamp lock-out codes and maintain records of runtime.

          - Maintenance reminder:  Boiler shall have the ability to display a yellow colored, customizable maintenance notification screen.  All notifications are adjustable by the installer based upon months of installation, hours of operation, and number of boiler cycles.

          - English Error codes:  Boiler shall have a user interface that displays a red error screen with fault codes that are displayed in English and include a date and time stamp for ease of servicing.

          - Anti-cycling control:  Boiler shall have the ability to set a time delay after a heating demand is satisfied allowing the boiler to block a new call for heat.  The boiler will display an anti-cycling blocking on the screen until the time has elapsed or the water temperature drops below the anti-cycling differential parameter.  The anti-cycling control parameter is adjustable by the installer.

          - Space Heating Night setback:  Boiler may be programmed to reduce the space heating temperature set point during a certain time of the day.

          - Freeze protection:  Boiler shall turn on the boiler and system pumps when the boiler water temperature falls below 45 degrees.  When the boiler water temperature falls below 37 degrees the boiler will automatically turn on.  Boiler and pumps will turn off when the boiler water temperature rises above 43 degrees.

          - Isolation valve control:  Boiler shall have the ability to control a 2-way motorized control valve.  Boiler shall also be able to force a fixed number of valves to always be energized regardless of the number of boilers that are firing.

          - BMS integration with 0-10V DC input:  The Control shall allow an option to Enable and control set point temperature or control firing rate by sending the boiler a 0-10V input signal.

          - Data logging:  Boiler shall have non-volatile data logging memory including last 10 lockouts, space heat run hours, domestic hot water run hours and ignition attempts.  All data should be visible on the boiler screen.

        - The boiler shall have a built in Cascade controller to sequence and rotate lead boiler to ensure equal runtime while maintaining modulation of up to 8 boilers of different btu inputs without utilization of an external controller.  The factory installed, internal cascade controller shall include:

          - Lead lag:  The Control module shall allow only one boiler to fire at the beginning of a call for heat.  Once the lead boiler is in full fire and the control calculates that additional heat is required it will call on an additional boiler as needed.

          - Efficiency optimization:  The Control module shall allow multiple boilers to simultaneously fire at minimum firing rate in lieu of Lead/Lag.

          - Front end loading:  The Control module shall allow the cascading and functional control of several non condensing Lochinvar products alongside the Knight FTXL.

          - Rotation of lead boiler:  The Control module shall change the lead boiler every hour for the first 24 hours after initializing the Cascade.  Following that, the leader will be changed once every 24 hours.

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 23 Section "Instrumentation and Control for HVAC."

        - Boiler operating controls shall include the following devices and features:

          - Set-Point Adjust:  Set points shall be fully adjustable by the installer.

Retain two subparagraphs below for steam boilers.

Retain one of three subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

          - Sequence of Operation:  Factory installed controller to modulate burner firing rate to maintain system water temperature in response to call for heat.

          - Sequence of Operation:  Boiler shall come standard with outdoor reset control which will control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At 10 deg F outside-air temperature, set supply-water temperature at 180 deg F; at 60 deg F outside-air temperature, set supply-water temperature at 140 deg F.

        - Burner Operating Controls:  To maintain safe operating conditions, burner safety controls limit burner operation and include:

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

          - High Temperature Limit:  Automatic and manual reset stops burner if operating conditions rise above maximum boiler design temperature.  Limit switch to be manually reset on the control interface.

In first subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

          - Low-Water Cutoff Switch:  Electronic probe shall prevent burner operation on low water.  Cutoff switch shall be manually reset on the control interface.

          - Blocked Inlet Safety Switch:  Manual-reset pressure switch field mounted on boiler combustion-air inlet.

          - High and Low Gas Pressure Switches:  Pressure switches shall prevent burner operation on low or high gas pressure.  Pressure switches to be manually reset on the control interface.

          - Blocked Drain Switch:  Blocked drain switch shall prevent burner operation when tripped.  Switch to be manually reset on the control interface.

          - Low air pressure switch:  Pressure switches shall prevent burner operation on low air pressure.  Switch to be manually reset on the control interface.

          - Optional Audible Alarm:  Factory mounted on control panel with silence switch; shall sound alarm for any lockout conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

        - Building Automation System Interface:

          - Boiler shall have the ability to receive a 0-10V system from a building management system and control by the following:

            - 0-10V DC input to control Modulation or Setpoint

            - 0-10V DC input from Variable speed Boiler pump

            - 0-10V DC output signal to a Variable speed system pump

            - 0-10V DC input Enable/Disable signal

          - Factory installed Modbus gateway interface to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.

      - ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article.  Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

        - Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

        - Single-Point Field Power Connection:  Factory-installed and factory-wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

        - Electrical Characteristics:

          - See Drawings

          - Voltage

            - 120V / 1PH

          - Frequency:  60 Hz

      - VENTING

Some boiler manufacturers offer venting kits that can be included with boiler.  Retain this Article if venting kit is included with boiler; otherwise, specify kit in Division 23 Section "Breechings, Chimneys, and Stacks."

        - Exhaust flue must be Category IV approved PVC, CPVC, PP or stainless steel sealed vent material from one of the approved manufacturers listed in the Installation and Operation manual.  Boilers exhaust vent length must be able to extend to 100 equivalent feet.

        - Intake piping must be of approved material as listed in the Installation and Operations manual.  Boilers intake pipe length must be able to extend to 100 equivalent feet.

        - Boiler venting and intake piping configuration shall be installed per one of the approved venting methods shown in the Installation and Operation manual.

        - Boilers using common venting must only include like models and the optional common vent damper.  Contact the factory for common vent sizing.

        - Boiler shall come standard with a flue sensor to monitor and display flue gas temperature on factory provided LCD display.

        - Refer to manufacturer’s Installation and Operations manual for detailed venting instructions and approved manufacturers.

      - SOURCE QUALITY CONTROL

        - Burner and Hydrostatic Test:  Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

        - Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

Retain paragraph below if Owner wants to witness source quality-control testing.

- EXECUTION

      - EXAMINATION

        - Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

          - Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in of piping and electrical connections.

        - Examine mechanical spaces for suitable conditions where boilers will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - BOILER INSTALLATION

Retain one of three "Equipment Mounting" paragraphs below.  Coordinate with Drawings and Sections specifying vibration and seismic controls.

Retain first "Equipment Mounting" Paragraph for equipment supported on cast-in-place concrete equipment bases without vibration isolation devices.

        - Install equipment on 4” concrete housekeeping pad.

        - Install gas-fired boilers according to NFPA 54.

        - Assemble and install boiler trim.

        - Install electrical devices furnished with boiler but not specified to be factory mounted.

        - Install control wiring to field-mounted electrical devices.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Install boilers level on concrete bases. Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

        - Install piping adjacent to boiler to allow service and maintenance.

        - Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

        - Connect gas piping to boiler gas-train inlet with union.  Piping shall be at least full size of equipment connection.  Provide a reducer if required.

        - Connect hot-water piping to supply and return boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

        - Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 23 Section "Steam and Condensate Heating Piping" or "Hydronic Piping."

        - Boiler Venting:

          - Install flue venting kit and combustion-air intake.

Delete option in subparagraph below if vent kit is specified in this Section.

          - Connect full size to boiler connections.  Comply with requirements in Division 23 Section “Breechings, Chimneys, and Stacks.

        - Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

      - FIELD QUALITY CONTROL

        - Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

        - Tests and Inspections:

          - Perform installation and startup checks according to manufacturer's written instructions.  Complete startup form included with Boiler and return to Manufacturer as described in the instructions.

          - Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

          - Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion.

          - Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

            - Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and water temperature.

            - Set field-adjustable switches and circuit-breaker trip ranges as indicated.

        - Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.

      - DEMONSTRATION

        - Engage a factory representative or a factory-authorized service representative for boiler startup.  Start-up sheet shall be completed and a copy shall be sent to the Engineer and the Manufacturer.  A combustion analysis shall be completed and the gas valve adjusted per the Installation and Operations manual and note in start-up report.

        - Factory representative or a factory-authorized representative shall provide Owners training to instruct maintenance personnel to adjust, operate, and maintain boilers.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 235216