Typical Specification

CBE-SPEC-03

Typical Specification for Lochinvar® Copper-Fin® Boiler

Models CB 0987 – CB 2067

The hot water BOILER shall be a LOCHINVAR COPPER-FIN Model CB(N,L)_________ having an input rating of _________ Btu/Hr, an output of _________ Btu/Hr and shall be operated on (Natural Gas) (L.P. Gas).

The water containing section shall be of a "Fin Tube" design, with straight copper tubes having extruded integral fins spaced seven (7) fins per inch.  The tubes shall terminate into a one piece, glass lined, cast iron header.  There shall be no bolts, gaskets or "O" rings in the head configuration.  There shall be access to the front header of the heat exchanger for the purposes of inspection, cleaning or repair.  The heat exchanger shall be mounted in a stress free jacket assembly in order to provide a "free floating design" able to withstand the effects of thermal shock.  The BOILER shall bear the ASME "H" stamp for 160 PSI working pressure and shall be National Board listed.  The complete heat exchanger assembly shall carry a ten (10) year limited warranty.

The combustion chamber shall be sealed and completely enclosed with "Loch-Heat™" ceramic fiberboard insulation.  A burner observation port shall be provided.  The burners shall be a premix design, constructed of high temperature stainless steel and fire on a horizontal plane.  The hot water BOILER shall use a combustion air blower(s) to precisely control the fuel/air mixture for maximum efficiency. Combustion air blowers shall operate for a pre-purge period before burner ignition and a post-purge period after burner operation.

The BOILER shall be constructed with a heavy gauge galvanized steel jacket assembly,  primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mils.  The jacket design shall allow single unit venting connection without the use of external draft hood devices.

The BOILER shall be certified and listed by C.S.A. International under the latest edition of the harmonized ANSI Z21.13 test standard for the US and Canada.  The BOILER shall comply with the energy efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.  The BOILER shall operate at a minimum of 81% thermal efficiency.

Standard operating controls shall include an electronic temperature controller to regulate boiler water temperatures and an immersion safety high limit control.

The standard control system shall include a Proven Pilot Hot Surface Ignition system with full flame monitoring capability.  Multiple main gas valves with redundant valve seats and built in low gas pressure regulators shall be supplied as standard.  Gas valves will be referenced to the combustion chamber to ensure proper air/gas mixture for efficient combustion.

Additional standard controls shall include a blocked flue/low air pressure switch for each fan, low voltage transformer for the control circuit, 7 amp circuit breaker for 24 VAC control circuit and an ASME pressure relief valve factory installed.  Natural Gas models come equipped with an automatic reset low gas pressure switch.  The manufacturer shall verify proper operation of the burners, all controls and the heat exchanger by connection to water and venting for a factory fire test prior to shipping.  A quality test report shall be shipped with each unit.

A 24 VAC control circuit and components shall be used.  All components shall be easily accessed and serviceable.  All components shall have multi-pin plug in type connectors to ease service, troubleshooting and lower removal and replacement cost.

The units control panel shall contain the temperature adjustment control, a on/off main power switch and indicating lights for call for heat, prepurge, trial for ignition, flame failure and alarm.

The BOILER shall be approved for indoor or outdoor installation.  The BOILER shall be approved for conventional venting (See mechanical detail) and shall be classified Category I, negative draft, non-condensing.  The vent material shall be a type "B" double wall.

The hot water BOILER shall have an independent laboratory rating for Oxides of Nitrogen (NOx) of less than 30 ppm corrected to 3% O2.

Maximum unit dimensions shall be: Length ________inches, Width ________inches and Height __________ inches.  Maximum unit weight shall be_________pounds.

The Firing Control System shall be ______ (Options Below).  Prefix "M" denotes staged Module Firing.

FIRING CONTROL SYSTEMS

M-9	Two Stage Hot Surface Ignition with Electronic Flame Supervision (Standard)

M-13	GE GAP/FM/IRI

M-7	California Code

Minnesota Code

Massachusetts Code

Kentucky Code

CSD-1 NOTE:  Due to the large discrepancy in CSD-1 requirements from state to state, please confirm to the factory all controls required in your jurisdiction.

01/11 – Printed in U.S.A.