Typical Specification for Lochinvar® Copper-Fin II® Water Heater Typical Specification

CFE-SPEC-03

Models 990,000 - 2,070,000 Btu/hr

The WATER HEATER shall be a LOCHINVAR COPPER-FIN II Model CF(N,L)_________PM having an input rating of _________ Btu/hr, a recovery capacity of _________ gallons per hour at a 100oF rise and shall be operated on (Natural Gas) (L.P. Gas).

The water containing section shall be of a "Fin Tube" design, with straight copper tubes having extruded integral fins spaced seven (7) fins per inch.  The tubes shall terminate into a one piece, glass lined, cast iron header.  There shall be no bolts, gaskets or "O" rings in the head configuration.  There shall be access to the front header of the heat exchanger for the purposes of inspection, cleaning or repair.  The heat exchanger shall be mounted in a stress free jacket assembly in order to provide a "free floating design" able to withstand  the effects of thermal shock.  The WATER HEATER shall bear the ASME "HLW" stamp for 160 PSI working pressure and shall be National Board listed.  The complete heat exchanger assembly shall carry a five (5) year limited warranty.  The WATER HEATER shall be equipped with a factory supplied circulating pump of sufficient capacity to ensure scale-free heater performance.  The pump shall be all bronze and provided for operation on 120 volt, 60 cycle, 1 phase power supply (unless otherwise specified).

The combustion chamber shall be sealed and completely enclosed with "Loch-Heat™" ceramic fiberboard insulation.  A burner/flame observation port shall be provided at both ends of the water heater.  The burners shall be a premix design and be constructed of high temperature stainless steel and fire on a horizontal plane.  The WATER HEATER shall have a multi-speed combustion air blower to precisely control the fuel/air mixture for maximum efficiency.

The WATER HEATER shall be constructed with a heavy gauge galvanized steel jacket assembly,  primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mils.  The jacket design shall allow single unit venting connection without the use of external draft hood devices.

The WATER HEATER shall be certified and listed by C.S.A. International under the latest edition of the harmonized ANSI Z21.10.3 test standard for the US and Canada.  The WATER HEATER shall comply with the energy efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.  The WATER HEATER shall operate at a minimum of 85% thermal efficiency.

The WATER HEATER shall be equipped with an Electronic Integrated Control Module with a microprocessor-based platform incorporating software customized for operation of the Lochinvar Copper-Fin II.  All internal safety, operating and ignition controls shall be included in the electronic integrated control module. The electronic integrated control module shall provide on/off control of the gas supply to the burner, operation of the combustion air blower, ignition of the gas-air mixture, flame proving, control of water temperature set points, and monitoring of all safety functions.

The WATER HEATER shall feature the “Smart System” control with a 2-line, 16 character LCD display, password security, pump delay with freeze protection, pump exercise and PC port connection.  The WATER HEATER shall allow 0-10 VDC input connection for BMS control and have built-in “Cascade” to sequence and rotate while maintaining stage firing of up to eight WATER HEATERS without utilization of an external controller.  Supply voltage shall be 120 volt / 60 hertz / single phase.

Local communication, programming and a display of operating and alarm status conditions shall be accessible through the Smart System control panel. The Smart System control panel shall contain an on/off main power switch, a digital display of a temperature functions, the operational status of the WATER HEATER, or an active alarm fault.  Data points visible in the digital display include inlet water temperature, outlet water temperature, water temperature differential, percent firing rate, setpoint temperatures, setpoint differential, minimum temperature, maximum temperature and maximum reset temperature.  Operational status shall be displayed for Off, Standby, Pre-purge, Ignition, Water Heating, and Post-purge.  Fault status shall be provided for high limit, gas pressure (optional), low water, blocked drain, louver proving, and air pressure switch status.  Modbus protocol (optional).

The 991,000 Btu/hr model shall proportional fire with three stages of burner input and the 1,260,000 through 2,070,000 Btu/hr models shall proportional fire with four stages of burner input.  The WATER HEATER Selected shall provide ______(3 or 4) individual stages of control.  Each stage shall provide for On/Off control of individual valves and increase/decrease control of the combustion air blower to maintain maximum efficiency at all stages of operation.

The standard control system shall include redundant Proven Pilot Hot Surface Ignition with full flame monitoring capability.  The Ignition system shall be able to function independently in the event of a failure in one system.  Multiple main gas valves with redundant valve seats and built in low gas pressure regulators shall be supplied as standard.  Gas valves will be referenced to the combustion chamber to ensure proper air/gas mixture for efficient combustion.

Additional standard controls shall include a flow switch, low air/blocked flue pressure switch for each fan, low voltage transformer for the control circuit, 7 amp circuit breaker and an ASME temperature and pressure relief valve.  All natural gas models will be equipped with an automatic reset low gas pressure switch.  The manufacturer shall verify proper operation of the burners, all controls and the heat exchanger by connection to water and venting for a factory fire test prior to shipping.  A quality test report shall be shipped with each unit.

A 24 VAC control circuit and components shall be used.  All components shall be easily accessed and serviceable.  All components shall have multi-pin, plug in type connectors to ease service, troubleshooting and lower removal and replacement cost. The WATER HEATER must be able to maintain approximately 50% operating capacity in the event of a failure of any one (1) control component, i.e.: gas valve, combustion air fan, ignition control, igniter or pressure switch.

The WATER HEATER shall be approved for indoor or outdoor installation.  The WATER HEATER shall be approved for Sidewall, DirectAire® Vertical, DirectAire Vertical with Sidewall Air Inlet, DirectAire Horizontal, Aire-Lock™ Direct Vent and conventional venting (See mechanical detail).  Venting shall be classified Category I, negative draft, non-condensing, to use type "B" double wall venting materials.  Direct Vent installations require the use of AL29-4C vent materials.

The WATER HEATER shall have an independent laboratory rating for Oxides of Nitrogen (NOx) of less than 20 ppm corrected to 3% O2.

Maxmum unit dimensions shall be: Length ________inches, Width ________inches and Height __________ inches.  Maximum unit weight shall be_________pounds.

The Firing Control System shall be ______ (Options Below).  Prefix "M" denotes staged Module Firing.

FIRING CONTROL SYSTEMS

M-9	Two Stage Hot Surface Ignition with Electronic Supervision (Standard)

M-7 	California Code

FOR PACKAGE SYSTEMS, ADD THE FOLLOWING:

The domestic hot water supply shall be provided by a LOCHINVAR COPPER-FIN II PACKAGED WATER HEATING SYSTEM Model_______________.  The package system shall consist of a Copper Fin II Water Heater, a jacketed and insulated Lock-Temp Storage Tank, an all bronze circulating pump, inlet and outlet ball valves and an ASME temperature and pressure relief valve.  Entire assembly shall be pre-piped, assembled and skid mounted, pressure tested and ready for installation.  Components shall be as follows:

The CIRCULATING PUMP shall be all bronze and operate on a 120 volt, 60 cycle, 1 phase power supply (unless otherwise specified).  The pump shall be wired to run with intermittent pump operation.

STORAGE TANK – Shall be a (vertical/horizontal) Lochinvar Lock-Temp® “Energy Saver” tank having a storage capacity of _____________gallons.  The tank shall be constructed with an inner chamber designed to receive all circulation to and from the water heater to eliminate turbulence in the tank.  The baffled tank shall supply 80% of tank capacity without a drop in outlet temperature.

The  STORAGE TANK  shall be constructed in accordance with (Standard/ASME) requirements, [if ASME, stamped and registered with the National Board of Boiler and Pressure Vessel Inspectors].  The storage tank shall have a working pressure of (125/150) psi [125 psi standard for ASME tanks].  The storage tank shall be (glass lined and fired to 1600°F to ensure a molecular fusing of glass and steel, and carry a five (5) year limited warranty).  The Lock-Temp Tank shall be constructed with a heavy gauge galvanized steel jacket assembly,  primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mils.  The jacket and tank base shall be a water tight construction with a built-in drain pan, complete with a ¾” drain connection to assist in protecting against damage in the event of a tank or component leakage.  The Storage Tank shall be completely encased in high density insulation of sufficient thickness to meet the energy efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.  The entire assembly shall be mounted on “I” beam skids to facilitate handling and installation.

05/11 – Printed in U.S.A.