Typical Specification

CGLD-SPEC-01

Typical Specification for Lochinvar Light Duty Charger Water Heaters

Models - 75,000 Btu/hr

The WATER HEATER shall be a LOCHINVAR "LIGHT DUTY CHARGER", Model ______________________ having an input rating of ______________ Btu/hr, a recovery capacity of _________ gallons per hour at a 100oF rise and shall be operated on (Natural Gas) (L.P. Gas).

The tank construction shall be of a high strength steel with a single-flue design for increased heat transfer efficiency.  The tank shall be constructed in accordance with standard construction requirements and shall be designed to withstand a hydrostatic test pressure of two times the working pressure without leakage.  The tank shall have a working pressure of 150 psi.  The tank shall be furnished with a handhole for ease of inspection, cleanout and service.  The interior of the tank shall be glass lined and fired to 1600o F to ensure a molecular fusing of glass and steel.  The tank shall be furnished with tank saver anodes to provide electrolytic protection and shall carry a three (3) year limited warranty.

The WATER HEATER shall be constructed with a heavy gauge steel jacket assembly.  The tank shall be completely encased in non-CFC polyurethane closed cell foam insulation to maximize heat retention and lower standby heat loss.  The exterior of the jacket assembly shall be finished in a 3-coat acrylic enamel finish.  The unit shall have a low silhouette, external draft diverter to allow easy connection to a Category I, negative draft, venting system.

The controls shall include an adjustable aquastat, a manual reset high limit control and a temperature and pressure relief valve.  The WATER HEATER shall be approved to provide 180o F water for sanitation, commercial and industrial operation.

The WATER HEATER shall be certified and listed by Underwriters Laboratories.  (The 65 gallon model shall be CSA certified.)  The water heater shall be certified for CSA Low Lead Content.  The WATER HEATER shall comply with the energy efficiency requirements for standby loss and thermal efficiency as specified in the latest edition of the ASHRAE 90.1 Standard.

6/15 – Printed in U.S.A.