Typical Specification

CLS-SPEC-02

Typical Specification for Lochinvar® Light Service Commercial

Electric Water Heaters

The WATER HEATER shall be Lochinvar Light Service Commercial Electric Water Heater Model ___________ with __________ gallon storage.  Rated at 6100 watt upper element, 6100 watt lower element, 277 Volts, Single Phase, wired for Simultaneous operation.  The tank shall be of standard construction with a 150 PSI working pressure and a 300 PSI test pressure.  The tank shall be glass lined and fired to 1600°F to ensure a molecular fusing of glass and steel.  A tank saver anode shall be installed in the tank for corrosion protection.  A 400°F rated high temperature dip tube shall be used to introduce water to the bottom of the tank.  The elements shall be incoloy sheath, immersion type with low watt density (75 watts per square inch maximum).  The tank shall be insulated with non-CFC polyurethane closed cell foam insulation to minimize heat loss and meet the requirements of the latest edition of ASHRAE 90.1b Energy Efficiency Standards.  The water heater jacket shall be heavy gauge steel with baked enamel finish.  Upper and lower access doors shall be provided for easy access to heating elements and temperature controls.  The water heater shall have internal fusing when current draw exceeds 120 amps.  The internal wiring shall be composed of solid copper wire having an insulation material rated at 600 V, 200C.  The water heater shall be factory supplied with an ASME temperature and pressure relief valve.

CONTROL CIRCUIT:  Surface mounted thermostats - Individual thermostats providing Simultaneous element control with a built-in manual reset high limit for over-temperature protection.  The heater may be field converted to Non-Simultaneous element control.

The water heater shall be certified and listed by Underwriters Laboratories.  The water heater shall be certified for CSA Low Lead Content.  The water heater shall be provided with a six-year limited tank warranty and a one year limited parts warranty.

03/16 – Printed in U.S.A.