Typical Specification

HP(ASME)-SPEC-05

Typical Specification for Lochinvar®

Compact ASME Hi-Power® Electric Water Heater

The WATER HEATER shall be LOCHINVAR COMPACT ASME HI-POWER® Model CH______________ with _________ gallons storage capacity, rated at __________kW, __________volts, _________ phase.  Heater to be completely insulated and jacketed for vertical installation.  The jacket shall be a round heavy gauge galvanized steel assembly, primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mills.  Jacket shall have a full-length element access panel and a hinged control panel access door for safety.  The jacketed tank assembly shall have an accessible drain.   The tank shall be factory insulated with a 3 inch thick high-density non-CFC polyurethane foam to meet the minimum stand-by loss requirements of the latest edition of ASHRAE 90.1 Energy Efficiency Standards.

The tank shall be of standard construction in accordance with ASME Boiler and Pressure Vessel Code requirements and shall be stamped and registered with the National Board of Boiler and Pressure Vessel Inspectors.  The tank shall be standard with 150 psi working pressure on all models.  The tank shall be glass lined with vitreous glass enamel and fired at 1600F to ensure a molecular fusing of glass and steel.  A combined magnesium tank saver anode with a powered anode shall be installed in the tank for corrosion protection.  A handhole clean-out shall be standard on all models to allow inspection and cleaning of the vessel.  Tank inlet and outlet water connections shall be 1-½” NPT.

The immersion heating elements shall be low watt density with an incoloy sheath for long life.  The heating elements shall mount in individual screw-in tank flanges. In accordance with U.L. requirements, water heaters with a current draw in excess of 120 amps shall be equipped with internal fusing.

All field electrical wiring connections to the water heater shall be made to a main terminal block. All internal wiring shall be made to solderless terminal lug wiring connections.  Wiring to be color coded for ease of servicing.  An ASME rated temperature and pressure relief valve shall be provided with the water heater.  The water heater shall be factory assembled, wired and tested. The entire water heater shall be U.L. Listed and provided with a 3 year limited warranty on the tank and a 1 year limited warranty on parts.

CONTROL CIRCUIT:

Immersion Thermostats and Contactors – Heating elements shall be switched by a magnetic contactor(s) operated by a fused 120 volt control circuit with an advanced electronic control.  The electronic control shall have an LCD readout which will display operational and diagnostic information.  Standard features include: Low Water Cutoff, Element Sensing and Night Setback.  The control shall be capable of supplying 180F water. The control circuit shall use a built-in transformer to reduce line voltage to 120 volts for operation of the control circuit components.  The control circuit shall include a manual reset safety hi-limit control to prevent over heating in the event of a component failure.

12/21 – Printed in U.S.A.