Typical Specification

HPT-SPEC-01

Typical Specification for Lochinvar® Thermal-Stor® Heat Pump Storage Tank

The HEAT PUMP STORAGE TANK shall be a Lochinvar Thermal-Stor tank, Model ____________ with vertical construction having a nominal storage capacity of _____ gallons.  The tank shall be constructed with an inner chamber baffle designed to receive all circulation to and from the water heater to eliminate turbulence in the tank.  The baffled tank shall supply 95% of tank capacity without a significant drop in outlet temperature.

The STORAGE TANK shall be constructed in accordance with ASME Boiler and Pressure Vessel Code requirements, “HLW” stamped and registered with the National Board of Boiler and Pressure Vessel Inspectors.  The tank shall be furnished with the following connections: two 3" Bolted Flange circulating connections, one 1-1/4" NPT relief valve connection, four 3/4" NPT aquastat openings and one 1" NPT drain connection.  The tank shall be furnished with a manway for ease of inspection, cleanout, and service.

The STORAGE TANK shall have a working pressure of 125 PSI.  The interior of the STORAGE TANK shall be glass lined and fired to 1600o F to ensure a molecular fusing of glass and steel, furnished with magnesium anode rods.

The STORAGE TANK exterior shall be constructed with a heavy gauge galvanized steel jacket assembly, primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mills.  The STORAGE TANK shall be completely encased in a minimum of 5" thick, high density polyurethane foam insulation and have an insulating value of R30.

The STORAGE TANK shall have a 10-year warranty against failure due to defects in materials or workmanship. All parts are warranted for 1 year. The limited warranty is in effect when the product is installed within the United States or Canada, provided it remains at its original place of installation. The warranty period shall begin on the date of installation OR 60 days after the date of manufacture if installation cannot be verified.

The jacket dimensions shall be _____" wide, _____" deep and ____" high.

06/2023 – Printed in U.S.A.