Typical Specification

TSJ-SPEC-06

Typical Specification for Lochinvar® Square Jacketed Lock-Temp® Storage Tank

The STORAGE TANK shall be a Lochinvar Lock-Temp "Energy Saver" tank, Model ___________ with (vertical/horizontal) construction and having a storage capacity of _____ gallons.  The tank shall be constructed with an inner chamber baffle designed to receive all circulation to and from the water heater to eliminate turbulence in the tank.  The baffled tank shall supply 80% of tank capacity without a drop in outlet temperature, regardless of rate of draw.

The STORAGE TANK shall be constructed in accordance with ASME Boiler and Pressure Vessel Code requirements, “HLW” stamped and registered with the National Board of Boiler and Pressure Vessel Inspectors.  The tank shall be furnished with the following connections: two 3" NPT circulating connections, one 2" NPT hot water outlet (3" NPT on 1250 gallon and larger), one 1 1/4" NPT relief valve connection, one 3/4" NPT aquastat opening, and one 1" NPT drain connection (special size connections may be specified).

The STORAGE TANK shall have a working pressure of 125 PSI (150 PSI).  The interior of the STORAGE TANK shall be (glass lined and fired to 1600oF to ensure a molecular fusing of glass and steel, furnished with magnesium anodes and carry a five (5) year limited warranty) (Cement lining and carry a five (5) year limited warranty).

The Lock-Temp Tank shall be constructed with a heavy gauge steel jacket assembly, primed and pre-painted on both sides with a minimum dry film thickness of 0.70 mills.  The jacket and tank base shall be a water tight construction with a built-in drain pan, complete with a 1" drain connection to assist in protecting against damage in the event of a tank or component leakage.  The STORAGE TANK shall be completely encased in a minimum of 3" thick fiberglass insulation to meet the efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.  The entire tank assembly shall be mounted on channel steel skids to facilitate handling and installation.

The jacket dimensions shall be _____" wide, _____" deep and ____" high.

Optional: Storage tanks shall be furnished with a (handhole, manway) for ease of inspection, cleanout, and service.

Note: A manway is standard on all Cement lined tanks.

06/24 – Printed in U.S.A.